| N100-24/N100-36 智能型NIMH电池充电器 |
| --- |
| 序号 | 项 目 | 单位 | 特 征 值 | 备 注 |
| 共同特性参数 |
| 01 | 额定输入 | V ac | 100~240Vac 50/60Hz |  |
| 02 | 输入电压范围 | V ac | 90~264Vac |  |
| 03 | 额定输入电流 | A | 0.8Arms | INPUT:220V OUTPUT:Full load |
| 04 | 最大输入功率 | W | 95 |  |
| 05 | 涓流维护电流（涓充电流） | A | < 0.1A |  |
| 06 | 主充纹波电流 | A | <0.15A | Input: 220Vac Output: Full load |
| 07 | 定时器设置 | hour | 8 |  |
| 08 | 快充/涓充转换条件 |  | dT/dt>=0.5 °C/min(TYP) 或 -(V >= 7mV /CELL(TYP) 或 Vmax>=1.6V/CELL 或Tmax>=50+-2°C 或 定时时间到（标准品为8小时） |  |
| 09 | LED指示灯标识 |  | 红灯常亮: 快充 绿灯常亮: 涓充/待机 绿灯闪亮：接口错误，充电异常 | 输出短路，电池反接，NTC温度传感器故障等问题发生时，LED绿灯闪亮。 |
| 10 | 输出短路保护 输出反接保护 | - | 有 有 | 短路电流 < 0.2A |
| 11 | 电源工作效率 | % | >80% | At max. load |
| 12 | 工作温度 | °C | -10 ~ +40 | Full load & natural convection. |
| 13 | 工作湿度 | %RH | < +90 | Relative humidity, non-condensing. |
| 14 | 存储温度 | °C | -40 ~ +70 |  |
| 15 | 存储湿度 | %RH | 0 ~ +95 | Relative humidity, non-condensing. |
| 16 | 冷却方式 | - | Natural convection |  |
| 17 | 温度系数 | % | <5% |  |
| 18 | 抗振动 |  | 5MM/50HZ/600S | Non-operating condition. |
| 19 | 抗冲击 |  | 1米高, 水泥地板, 3次 | Non-operating condition. |
| 20 | 重量 | g | 约650 |  |
| 21 | 外形尺寸 | mm | 约170X71X51毫米 | Casing only |
| 22 | 输入输出线及插接头 | - | 输入由客户自定 输出1+ 2- 3NTC |  |
| 23 | 最大溫升 | °C | < 40 on casing | At any line and Max. Load |
| 24 | 安全规格标准 | - | ICE335 UL1310 |  |
| 25 | 产品已取得的安规证书 | - | CE cUL |  |
| 26 | 防静电等级 | kV | 8.0 |  |
| 27 | 隔离耐电压 | V | i/p to o/p: 3000 (1 min.) | For final unit, cut-off current =10mA |
| 各型号输出特性 |
| 28 | 型号 |  | N100-24 | N100-36 |
| 29 | 额定输出电压 |  | 28V | 42V |
| 30 | 输出电压范围 | V dc | 20-36V | 30-50V |
| 31 | 适用电池规格 | Ah | 24V 3~20Ah 20串 NIMH | 36V 3~20Ah 30串 NIMH |
| 32 | 恒流充电电流(主充电流) | A | 1.85 A (( 0.2A) | 1.85A（( 0.2A） |
| 33 | 最大输出功率 | W | 65W | 85W |

| N100-24/N100-36 Smart NIMH Battery-Pack Charher |
| --- |
| General Information |
| No. | Item | Unit | Specification | Remark |
| 01 | Rating Input Voltage | V ac | 100~240Vac 50/60Hz |  |
| 02 | Input Voltage Range | V ac | 90~264Vac |  |
| 03 | Rating Input Current | A | 0.8Arms | INPUT:220V OUTPUT:Full load |
| 04 | Rating Input Power | W | 95 |  |
| 05 | Trickle charge current ( after main charge cut-off) | A | <0.1A |  |
| 06 | Main charge current ripple | A | <0.15A | Input: 220Vac Output: CV 28V CV 42V |
| 07 | Build-in Timer | Hour | 8 |  |
| 08 | Main Charge Cut-off Conditions |  | dT/dt>=0.5 °C/min(TYP) or -(V >= 7mV /CELL(TYP) or Vmax>=1.6V/CELL or Tmax>=50+-2°C or Time out |  |
| 09 | LED Indication |  | RED: Main charge GREEN: Finish or idle GREEN LED FLASH: Errors | Error: Output short-circuit. Battery reversed, NTC errors…… |
| 10 | Output Short-circuit Protection Output Reverse Protection | - | yes yes |  |
| 11 | Efficiency | % | >80% | At max. load |
| 12 | Operate Temp. | °C | -10 ~ +40 | Full load & natural convection. |
| 13 | Operate Humidity | %RH | < +90 | Relative humidity, non-condensing. |
| 14 | Storage Temp. | °C | -40 ~ +70 |  |
| 15 | Storage Humidity | %RH | 0 ~ +95 | Relative humidity, non-condensing. |
| 16 | Cooling | - | Natural convection |  |
| 17 | Temp Fact | % | Less than 5% |  |
| 18 | Vibration |  | 5MM/50HZ/600S | Non-operating condition. |
| 19 | Impach |  | 1 meter drop test >= 3 times | Non-operating condition. |
| 20 | Weigth | g | 650 |  |
| 21 | Size | mm | 170X71X51 | Casing only |
| 22 | Input/Output Cable and Connecters. | - | AC plug: Defined when order DC plug: 3-pin type 1+ 2- 3NTC | Note: UL mark and CE mark can’t be place on Lable at the same time, because AC plug is fixed on product. |
| 23 | Temp. Rise | °C | < 40 on casing | At any line and Max. Load |
| 24 | Safety Standard Meeted | - |  |  |
| 25 | Safety Approvals passed | - | CE cUL |  |
| 26 | ESD | kV | 8.0 |  |
| 27 | HI-POT | V | i/p to o/p: 3000 (1 min.) | For final unit, cut-off current =10mA |
| Individual Specification for each model |
| 28 | Models |  | N100-24 | N100-36 |
| 29 | Rating output voltage | V dc | 28V | 42V |
| 30 | Output voltage range | V dc | 20~36V | 30~50V |
| 31 | Battery-pack Suited | Ah | 24V 3~20Ah 20 Serial NIMH | 36V 3~20Ah 30 Serial NIMH |
| 32 | Main charge current | A | 1.85A (( 0.2A) | 1.85A（( 0.2A） |
| 33 | Max Output Power | W | 65W | 85W |