Fiberglass Filter Felt Data

玻 纤 滤 棉 技 术 参 数

| Specification |  |
| --- | --- |
| Appearance | Bulky mass with green and white (or both white) surfaces. |
| Thickness | 30mm, 50mm, 100mm (Special sizes are available on request.) |
| Width | 300-2100mm |
| Density | 3-8kg/m 3 |

| Type | Free state thickness(mm) | Pressure drop at different air flow rate (Pa) |  |  | Efficiency vs particle size (%) |  |  | Dust holding capacity (g/m 2) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1.3 | 2.6 | 3.9 | >=2micro | >=5micro | >=10micro |  |
| PA-30 | 30 | 15 | 29 | 44 | 31 | 62 | 71 | 1100 |
| PA-50 | 50 | 16 | 31 | 47 | 35 | 68 | 80 | 1850 |
| PA-100 | 100 | 23 | 41 | 54 | 57 | 81 | 92 | 3200 |