GUANGZHOU SUN HOL YWIND AIR CLEANING PRODUCTS CO,.LTD.

ADD: 3.,SHANGNAN INDUSTRIAL ZONE,TAIHE TOWN,BAIYUN

DISTRICT,GUANGZHOU CITY,GUANGDONG PROVINCE,CHINA.

TEL:+86-20-87428521-807        FAX:+86-20-87422482

HTTP://WWW.GZSHY.COM      EMAIL: JUDYLINE@163.COM

# Black Media Test Report

| Dimensions&Tech data | TYPE |  |  | Conclusion |
| --- | --- | --- | --- | --- |
|  | BM-20 | BM-30 | BM-40 |  |
| Thickness mm | 6 | 8 | 10 | Eligibility |
| Standard roll widths cm | 100;200; | 100;200; | 100;200; | Eligibility |
| Standard roll length m | 20 | 20 | 20 | Eligibility |
| Colour(air inlet/outlet) - | Black | Black | Black | Eligibility |
| Operating Data |  |  |  |  |
| Arrestance(A;EN-779) % | 65% | 85% | 94% | Eligibility |
| Efficency class(EN-779) - | G2 | G3 | G4 | Eligibility |
| Test air velocity m/s | 2.0 | 1.5 | 1.5 | Eligibility |
| Air flow(on 1m²of medium) m³/h | 5400 | 5400 | 5400 | Eligibility |
| Initial pressure drop Pa | 20 | 25 | 30 | Eligibility |
| Max recommended pressure dorp Pa | 180 | 250 | 250 | Eligibility |
| Max operating temperature ℃ | 100℃ | 100℃ | 100℃ | Eligibility |
| Flame resistance rating(DIN-53438) - | F1 | F1 | F1 | Eligibility |
| Dust holding capacity g/m³ | 400 | 500 | 600 | Eligibility |

Date: 2006-8-15